Summary

Formic acid and acetic acid are among the most critical indoor air pollutants known to cause damage to heritage collections. This Ph.D. project examined the route of organic acids in storage buildings from emission sources, such as the collections themselves, to the removal through air exchange with ambient, air filtration in mechanical ventilation systems, and deposition onto interior surfaces. The aim was to establish the fate of formic acid and acetic acid in storage buildings and to determine control methods for the protection of heritage collections from corrosive organic acids.

The area-specific emission rates of formic acid and acetic acid from six naturally aged wood and paper samples and from a wood packaging material used to transport and storage collections were measured at laboratory conditions. The emission rate ranged from 10 to 300 µg m-2 h-1 at indoor room conditions (23ºC, 50% RH). The study also demonstrated that a decrease in temperature from normal room conditions to 10ºC reduced the emission rate of organic acids 2-4 times from wood and paper, whereas a decrease in the RH from 50% to 20% reduced the emission rate with a factor 2 or more. A similar organic acid behaviour was observed in unoccupied storage buildings where the decrease in temperature from summer to winter led to a reduction in the concentration of organic acids in air.

The spatial distribution in temperature, moisture and organic acids were measured in one storage building belonging to the Royal Library in Denmark (with a mechanical ventilation system), and in two rooms in the shared storage facility at the Centre for Preservation of Cultural Heritage in Vejle (with semi-passive climate control). The spatial temperature and moisture distribution were almost uniform except for a weak vertical temperature gradient causing a RH gradient opposite to that of temperature. The spatial organic acid distribution showed areas in the storage building with semi-passive climate control where incomplete mixing caused a local accumulation of organic acids. However, the survey demonstrated that both storage buildings provided acceptable temperature and moisture distributions without problematic microclimates, and with an acceptable air quality performance irrespective of the ventilation form.

An intervention study was additionally carried out in the two buildings, in order to measure the removal efficiency of two commercially available activated carbon filters in situ. The organic acid removal efficiency of a desiccant silica gel rotor used for dehumidification, and the passive adsorption onto a clay brick wall, were also measured. The intervention study demonstrated that the organic acid removal efficiency of the filters depend on the airflow through the filter and that the performance varies considerably in situ from the removal efficiency obtained in a laboratory. The desiccant silica gel rotor efficiently removed 98-100% acetic acid from the air while the clay brick wall reduced the concentration of acetic acid close to the wall with 56%.

The storage buildings examined in this project maintained almost the same temperature and RH conditions indoor however, the store with a mechanical ventilation system consumed almost 60 times more energy for outdoor air filtration and climate control than the store with semi-passive climate control. The results underlined that storage buildings with semi-passive climate control provide acceptable climate and air quality conditions and reduces the energy use for the preservation of collections in storage.

All data was collated into a Monte Carlo simulation to examine the fate of organic acids in heritage collection storage buildings. The simulations showed that formic acid and acetic acid would deposit onto interior surfaces despite the use of active air filtration, and with the continued risk of causing damage to heritage collections.

Dansk resumé

Organiske syrer i museumsmagasiner og deres konsekvens for luftkvalitet, energiforbrug og bevaringen af vore kulturarvssamlinger

De organiske forbindelser, myresyre og eddikesyre, er blandt de mest skadelige luftforureningsstoffer indendørs i forhold til nedbrydningen af vore kulturarvssamlinger. Dette ph.d.-projekt har undersøgt tilstedeværelsen og fordelingen af organiske syrer i indeklimaet i magasinbygninger til opbevaring af kulturarv, fra kilde til bortfjernelse. Selve samlingerne, samt træholdigt pakkemateriale og inventar, kan være en væsentlig kilde til luftforureningen indendørs. Bortfjernelse sker igennem luftskiftet, luftfiltrering i mekaniske ventilationsanlæg samt ved deponering på indvendige overflader. Målet med ph.d.-projektet var at kortlægge forureningsstoffernes rute, for at kunne udpege de mest effektive kontrolmetoder til beskyttelse af vore kulturarvssamlinger mod nedbrydning.

Afgasningsraten af myresyre og eddikesyre fra seks naturligt ældede træ- og papirprøver, og fra træemballagen, der anvendes til transport og opbevaring af genstande på magasinernes kompaktreoler, blev målt i et laboratorium. Emissionsraten varierede fra 10 til 300 µg m-2 h-1 under normale indendørs klimaforhold (23ºC, 50% RF). Undersøgelsen viste desuden, at et fald i temperatur fra normale indendørs klimaforhold til 10°C formindsker emissionsraten af ​​organiske syrer 2-4 gange, mens et fald i den relative luftfugtighed fra 50% RF til 20% RF formindsker emissionsraten 2 gange eller mere. Den samme tendens blev observeret i magasinbygninger uden komfortopvarmning, hvor en sænkning i temperaturen fra sommer til vinter medførte et 2-3 gange fald i koncentrationen af ​​organiske syrer i luften.

Den rumlige fordeling og variation i temperatur, luftfugtighed og koncentration af organiske syrer blev målt detaljeret over et år for magasinrum beliggende i to forskellige magasinbygninger. Det ene magasin tilhører Det Kongelige Bibliotek (styret med et mekanisk ventilationsanlæg), mens det andet magasin tilhører Center for Bevaring af Kulturarv i Vejle (semi-passiv klimastyret). I magasinet i Vejle blev to magasinrum undersøgt. Den rummæssige temperatur- og fugtfordeling var næsten ensartet i de to bygninger, bortset fra en svag lodret temperaturgradient, der forårsager en omvendt gradient i relativ luftfugtighed. Den rumlige fordeling af organiske syre viste en uensartet luftopblanding i det ene rum i bygningen med semi-passiv klimakontrol. Dette gav anledning til luftlommer med lokale ophobninger af organiske syrer. På trods af dette viste undersøgelsen, at uanset ventilationsform, opretholder begge bygninger en acceptabel temperatur- og fugtfordeling uden problematisk mikroklima, og med en acceptabel luftkvalitet.

Effektiviteten af luftrensning med kulfiltrering blev afprøvet i et interventionsstudie in situ i begge bygninger. T​o forskellige kulfilter-typer blevet testet. Desuden blev en silica-gel adsorptionsaffugters evne til at fjerne eddikesyre fra luften afprøvet i laboratoriet, og passiv luftrensning ved adsorption på en lervæg blev afprøvet i et testrum. Interventionsstudiet viste, at effektiviteten af filtrene afhænger af luftstrømningshastigheden gennem filteret, og at den varierer betydeligt in situ fra effektiviteten målt under kontrollerede laboratorieforhold. Affugteren kunne fjerne stort næsten alt (98-100%) eddikesyre fra luften, mens lervæggen reducerede luftens koncentration af ​​eddikesyre med 56% i umiddelbar nærhed af vægoverfladen.

De klimamæssige forhold var næsten ens i de to magasinbygninger undersøgt i dette projekt. Energiforbruget var til gengæld næsten 60 gange større i bygningen med et mekanisk ventilationsanlæg, til udendørsluftfiltrering og klimastyring, end i bygningen med semi-passive klimakontrol. Resultaterne understreger at bygninger med semi-passiv klimastyring sikrer acceptable klima- og luftkvalitetsforhold og et lavere energiforbrug til bevaringen af kulturarvssamlinger.

Alt data fra projektet blev samlet i en Monte Carlo simulering for at analysere og illustrere variationen i koncentrationen af ​​organiske syrer i indeklimaet i kulturarvsmagasinbygninger. Simuleringerne viste, at myresyre og eddikesyre deponeres på indvendige overflader trods brugen af ​​aktiv luftfiltrering, hvilket medfører en forsat risiko for at forårsage skade på kulturarvssamlinger.